# 3-Way Valve Control & Communication Validation

| Prepared By NOAH OVIKIAN | Prepared Date 9/20/2026 |
| --- | --- |
| Reviewed By ETHAN HENDERSON | Review Date |
| Approved By | Approval Date |

Contents

1	Introduction	3

1.1	Purpose	3

1.2	Acronyms & Units	4

1.3	Instrument & Signal Tags	Error! Bookmark not defined.

1.4	Terminology & Assumptions	Error! Bookmark not defined.

1.5	DI Water Cooling Skid P&ID	Error! Bookmark not defined.

1.6	Control Philosophy	Error! Bookmark not defined.

1.7	Control System Framework	Error! Bookmark not defined.

2	System Operation	Error! Bookmark not defined.

2.1	System Modes	Error! Bookmark not defined.

2.1.1	Simplex Mode	Error! Bookmark not defined.

2.1.2	Manual Fan Control (MFC) Mode	Error! Bookmark not defined.

2.1.3	Manual Control Valve Actuation (MCVA) Mode	Error! Bookmark not defined.

2.1.4	Automatic Pump Cycling (APC) Mode	Error! Bookmark not defined.

2.1.5	Default Mode of Operation	Error! Bookmark not defined.

2.2	System States	Error! Bookmark not defined.

2.2.1	System Offline	Error! Bookmark not defined.

2.2.2	System Stasis	Error! Bookmark not defined.

2.2.3	System Standby	Error! Bookmark not defined.

2.2.4	System Active	Error! Bookmark not defined.

2.2.5	System Fault	Error! Bookmark not defined.

2.3	System Sequences	Error! Bookmark not defined.

2.3.1	System Cold Start Sequence	Error! Bookmark not defined.

2.3.2	System Standby Startup Sequence	Error! Bookmark not defined.

2.3.3	System Fault Startup Sequence	Error! Bookmark not defined.

2.3.4	System Pulse Sequence	Error! Bookmark not defined.

2.3.5	System Shutdown Sequence	Error! Bookmark not defined.

2.4	Fault Management	Error! Bookmark not defined.

3	Temperature Control System	Error! Bookmark not defined.

3.1	Signal Processing	7

3.2	Temperature Regulation	9

3.3	Manual Operation	11

4	Hydraulic Control System	12

4.1	Signal Processing	12

4.2	Low Thresholds & Failure Classification	13

4.3	Hydraulic Failure Pump Turnover	14

4.4	Lifecycle Pump Monitoring & Turnover	15

4.5	Manual Operation	15

5	Vessel Level Control System	16

5.1	Signal Processing	16

5.2	Level Monitoring	16

5.3	Redundancy Control	16

6	Conductivity Control System	17

6.1	Signal Processing	17

6.2	Conductivity Monitoring	17

6.3	Redundancy Control	17

# Introduction

## Purpose

The purpose of this document is to describe process, methods and philosophy for controlling the Deionized (DI) Water Variable Frequency Drive (VFD) Cooling Skid for the Toshiba Mitsubishi-Electric Industrial Systems Corporation (TMEIC). This document shall act as the primary method of communication when describing the process, methods, and philosophy of skid control, serving to align all parties and entities involved in the engineering, procurement, construction, and operation of the cooling skid. All changes to the process, methods and philosophy of control of the cooling skid, shall be formalized through this document.

## Acronyms & Units

The following is a list of acronyms and units that are used throughout this document:

- DI: Deionized

- VFD: Variable Frequency Drive

- TMEIC: Toshiba Mitsubishi-Electric Industrial Systems Corporation

- PLC: Programable Logic Controller

- P&ID: Piping and Instrumentation Diagram

- HMI: Human Machine Interface

- SP: Setpoint

- GPM: Gallons Per Minute

- V: Volts

- mA: Milliamps

- cm: Centimeters

- μS: Micro Siemens

- W: Watts

- s: Seconds

- ms: Milliseconds

- BOOL: Single bit Boolean data type

- INT: Signed 16-bit Integer data type

- WORD: Unsigned 32-bit integer data type

- REAL: Signed 32-bit float data type

- DINT: Signed 32-bit integer data type

- UDINT: Unsigned 32-bit integer data type

## Test Objectives

This control narrative briefly refers to instruments by their tags. Instrument tags shall be defined in the sponsor specification document, and the signals shall be defined in the PLC point list (TMEIC-TAMU-ECEN-DOC-02).

All instrument tags shall have a prefix “P” followed by an integer (1-17). Additionally, the integer may be followed by a letter to specific multiple instruments of the save time. (For example, P1A and P1B are two pumps). For more details, please reference the sponsor specification document

This control narrative refers to signals produced outside and within the PLC by their tags. These signals include switch signals, physical signals, internal signals, alarm signals, and fault signals. All signals shall carry information to, from, and within various entities, including, but not limited to, the HMI, the PLC, and various field instruments. Physical signals shall carry data over a physical medium, either through a 4-20 mA signal, or a 0-24V signal. All other signals shall carry data digitally by various sized buses of bits.

All signals mentioned in this document shall be referenced by their tags, as defined in the PLC point list. Below is a brief description of the naming conventions used for all signals.

All physical signal tags shall have a prefix “PHY-” followed by an integer, inclusively ranging 1-21. “PHY-1” is an example of a tag for a physical signal. For more details, please see PLC Point List

All switch signals tags shall have a “SW-” prefix, followed by an integer, inclusively ranging from 1 to 21. “SW-1” is an example of a tag for a switch signal. For more details, please see PLC Point List

All internal signal tags shall have a “SIG-” prefix, followed by an integer. The integer following the prefix shall range, inclusively, from 1 to 25. “SIG-1” is an example of a tag for a internal signal. For more details, please see PLC Point List.

All alarm signal tags shall have a “ALM-” prefix, followed by an integer. The integer following the prefix shall range, inclusively, from 1 to 17. “ALM-1” is an example of a tag for an alarm signal. For more details, please see the PLC Point List.

All fault signals tags shall have a “FLT-“  prefix, followed by an integer. The integer following the prefix shall range, inclusively, from 1 to 17. “FLT-1” is an example of a tag for an alarm signal. For more details, please see the PLC Point List.

## Test Rules

# Pretest Validation

## Role Certification

Signature of all individuals listed below shall hereby certify that each individual is present at the date of test, is available to perform the test and related test duties according to the test rules and test procedures, and shall be present to perform the test and related test procedures according to the test rules and test procedures

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Evaluator | Robert Parker |  |  |
| Evaluator | Noah Ovikian |  |  |

## Notary

Signature below certifies that the individual shall act as the notary for this test. Their signature shall be required on all components of this test documentation.

|  |  |  | Date |
| --- | --- | --- | --- |

## Test Date

Signature confirms date of validation is 9/27/2026

| Notary |  |  | Date |
| --- | --- | --- | --- |

## Pretest Checks

| Step | Description | Result |
| --- | --- | --- |
| 1 | PLC & HMI Energized | ☐Pass ☐Fail |
| 2 | Latest PLC Program Ready, Downloaded, & Error Free | ☐Pass ☐Fail |
| 3 | Latest HMI Software Ready, Downloaded, & Error Free | ☐Pass ☐Fail |
| 4 | 3-Valve 4-20mA output signal connected to Module 750-0554, Position 12, Channel 1 | ☐Pass ☐Fail |
| 5 | 3-Way Valve 4-20mA feedback output signal connected to Module 750-0455, Position 8, Channel 3 | ☐Pass ☐Fail |

| Notary |  |  | Date |
| --- | --- | --- | --- |

# Test Procedure

## Test Initialization Time

| Step | Description |  |  | Result |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Write time (CST) of test initialization |  |  |  |  |
| Notary |  |  |  |  | Date |

## Valve Stroke Test

Valve stroke test shall ensure that the valve has full mobility through PLC control. Time of actuation and measured valve position shall be recorded.

| Step | Description | Result |
| --- | --- | --- |
|  | Actuate Valve with to 0° | ☐Done ☐Fail |
|  | Record feedback signal observed on PLC (position in °) |  |
|  | Valve is physically observed to be 100% Open |  |
|  | Actuate Valve to 90° |  |
|  | Record time of actuation in seconds |  |
|  | Record feedback signal observed on PLC (position in °) |  |
|  | Valve is physically observed to be 100% Closed |  |
|  | Actuate Valve to 0° |  |
|  | Record time of actuation in seconds |  |
|  | Record feedback signal observed on PLC as 4-20mA signal. |  |
|  | Valve is physically observed to be 100% Open |  |

| Notary |  |  | Date |
| --- | --- | --- | --- |

## Valve Response Observation

| Step | Description | Result |
| --- | --- | --- |
| 1 | Actuate Valve with to 0° | ☐Done ☐Fail |
|  | Record time of actuation in seconds |  |
| 2 | Record feedback signal observed on PLC (position in °) |  |
| 3 | Valve physically changed positions towards close direction |  |
| 4 | Actuate Valve to 22.5° |  |
|  | Record time of actuation in seconds |  |
|  | Record feedback signal observed on PLC (position in °) |  |
|  | Valve physically changed positions towards close direction |  |
|  | Actuate Valve to 45° |  |
|  | Record time of actuation in seconds |  |
|  | Record feedback signal observed on PLC (position in °) |  |
|  | Valve physically changed positions towards close direction |  |
|  | Actuate Valve to 67.5° |  |
|  | Record time of actuation in seconds |  |
|  | Record feedback signal observed on PLC (position in °) |  |
|  | Valve physically changed positions towards close direction |  |
|  | Actuate Valve to 100° |  |
|  | Record time of actuation in seconds |  |
|  | Record feedback signal observed on PLC (position in °) |  |
|  | Valve physically changed positions towards close direction |  |

sensors are functioning, the median value of the REAL-valued RTD signals shall be considered as the measured coolant temperature (SIG-6). If two (2) or more of the REAL-valued RTD signals are the same, then that value shall be considered as SIG-6. If two (2) of three (3) sensors are functioning, the average value of the two (2) functioning REAL-valued RTD signals shall be considered as SIG-6. If less than two (2) of three (3) sensors are function, FLT-7 shall be engaged, and the last read measured coolant temperature shall be considered as SIG-6 for measurement continuity during system shutdown.

The measured coolant temperature shall be regulated by controlling flow entering the heat exchanger through the control valve. The valve open percentage shall be stored as a REAL-valued signal (SIG-9) within the PLC. SIG-9 will then be converted into a WORD-valued 4-20mA output signal (PHY-16), shall be fed to the physical control valve for control actuation.

## Temperature Regulation

A multi-stage control scheme shall be implemented, in which the control shall be opened to convert 0%, 33.4%, 66.7%, or 100% of the total flow as throughput flow. It shall be assumed henceforth that throughput flow is directly proportional to the open percentage of the valve. (For example, a 33.4% open control valve shall correlate to 33.4% throughput flow) Additionally, the heat exchanger itself shall be fitted with two (2) pairs of fans to assist with convection cooling. These fans shall be controlled binarily through a digital 0-24V signal (PHY-12, PHY-13). When throughput flow is greater than 0%, both pairs of fans shall be activated, and when throughput flow is at 0%, both pairs of fans shall be deactivated.

Valve actuation shall be controlled by comparing the measured temperature with maximum threshold.  The resulting comparison shall be referred to as the differential temperature (ΔT) and is the difference between the measured temperature and the maximum threshold.

The openness of the control valve shall be actuated in four (4) stages, including the ground stage. Each stage shall have a unique SP which increments the stage, and all stages shall share a SP, that resets the ground stage.

At ground stage, the control valve shall be 0% open, and the heat exchanger fans shall be disengaged. To advance from the ground stage to the first stage, the ΔT SP must be less than equal to 6°C.

At the first stage, the control valve shall be 33.4% open, and the heat exchanger fans shall be engaged. To advance from the first stage to the second stage the ΔT SP must be less than or equal to 4°C.

At the second stage, the control valve shall be 66.7% open, and the heat exchanger fans shall be engaged. To advance from the second stage to the third stage the ΔT SP must be less than or equal to 1°C.

At the third stage, the control valve shall be 100% open, and the heat exchanger fans shall be engaged.

The reset from any stage (that is going from the first, second, or third stage to the ground stage, the ΔT SP must be greater than or equal to 8°C.

Stages must increase incrementally (e.g. the controller cannot jump from stage 0 to stage 3 immediately, without going through stage 1 and stage 2), and stages can only be reset back to the ground stage (e.g. stage 3 cannot be decremented to stage 2)

Table 1: Actuation Schedule of the control valve, along with differential temperature setpoints, and ground setpoint.

| Current Stage | Open % | Next Stage | ΔT SP | Reset ΔT SP |
| --- | --- | --- | --- | --- |
| 0 (Ground) | 0% | 1 | ≤ 6°C | ≥ 8°C |
| 1 | 33.4% | 2 | ≤ 4°C |  |
| 2 | 66.7% | 3 | ≤ 1°C |  |
| 3 | 100% | - | - |  |

This staging method allows for multistage operation of the temperature controller without causing hysteresis.

Should the differential temperature reach or become less than 1°C and remain at that level for a duration of at least 10 seconds, a high coolant temperature alarm (ALM-1) be engaged. At any point where ALM-1 is engaged, should the measured coolant temperature fall below 1°C, ALM-1 shall be disengaged.

Should the differential temperature become equal to or less than 0°C but then rise above 1°C before 5 seconds has elapsed, ALM-1 shall remain disengaged.

Should the differential temperature reach or become less than 0°C, ALM-1 shall be engaged, and shall only be disengaged once the differential temperature rises above 1°C.

Should the differential temperature reach or become less than 0°C and remain at or less than 0°C for at least 5 seconds, the system shall engage the temperature fault (FLT-1), and the system shall shut down.

Should the differential temperature reach or become less than 0°C but then rise above 0°C before 5 seconds elapse, FLT-1 remain disengaged.

The time durations for both the engagement of the alarm and fault signals allow prevents accidentally alarm and fault triggers from noise, while also allowing for transients to be worked out within the cooling skid.

## Manual Operation

The control valve may be manually actuated if MCVA mode is engaged. When MCVA mode is engaged, all automatic control shall be overridden by the operator, so long as the PLC is in run mode. When engaged, the operator may choose to change the openness percentage of the valve by inputting in a real value inclusively between 0 and 100 into the manual open valve signal (SIG-27). Any value below 0 shall be considered 0, and any value above 100 shall be 100. This signal shall then be converted into a WORD-valued 4-20mA output signal (PHY-16) and shall be fed to the physical control valve for control actuation.

Each fan pair may be manually controlled by the operator if MFC mode is engaged. When MFC mode is engaged, all automatic control of the fans shall be overridden by the operator, so long as the PLC is in run mode. When MFC mode is engaged, operator may engage or disengage the fans using switches SW-8 and SW-9 for fan 1 and 2 respectively. When MFC mode is engaged switches shall control the 0-24V BOOL-values physical signals (PHY-12 and PHY-13) to actuate the fans according to the operator’s commands.

Note, engaging in MFC or MCVA may cause damage to the VFD/heat source and should only be done in a controlled environment, for a limited time.

# Hydraulic Control System

## Signal Processing

System hydraulics shall be observed by three parameters: pump power, flow, and pressure. Pump voltage shall be communicated from the active pump (P1A/P1B) to the PLC through a 4-20mA WORD-valued signal. Specifically, the primary pump voltage shall be communicated through WORD-valued signal PHY-18 and the secondary pump current shall be communicated through WORD-valued signal PHY-20.

Additionally, the pump current shall be communicated from the active pump to the PLC through a 4-20mA WORD-valued signal. Specifically, the primary pump current shall be communicated through WORD-valued signal PHY-19 and the secondary pump current shall be communicated through WORD-valued signal PHY-21.  Any pump signal that exceeds 20.5 mA or falls below 3.5 mA shall be considered a bad signal, engaging ALM-7 or ALM-8 (respective of the pump). The voltage and current WORD-valued signals of the primary pump shall be converted into a REAL-valued signal (SIG-32, and SIG-33 respectively). Additionally, the voltage and current WORD-valued signals of the secondary pump shall be converted into a REAL-valued signal (SIG-34, and SIG-35 respectively).

The voltage and current shall be multiplied together to calculate the power produced by the primary and secondary pump, and shall be stored as a REAL-value signal (SIG-13 and SIG-14, respectively)

Only the power of the active pump shall be considered as the measured pump power (SIG-5). Flow shall be sampled by an ultrasonic flowmeter (P13) and communicated to the PLC through a 4-20mA WORD-valued signal (PHY-1). A flow signal that exceeds 20.5 mA or falls below 3.5 mA shall be considered a bad signal, engaging alarm ALM-13. The WORD-valued flow signal shall be converted into a REAL-valued signal (SIG-8)   System pressure shall be observed binarily as to be low or nominal. System pressure status shall be communicated to the PLC through a 0-24V signal (PHY-17). System pressure shall be passed through a hysteresis filter before being considered as the final pressure measurement (SIG-16 and SIG-22)

Primary and secondary pumps shall be engaged using a 0-24V signal from the PLC (PHY-14, PHY-15). One and only one pump may be active during the operation. A pump is considered active if it receives a 24V signal from the PLC.

## Low Thresholds & Failure Classification

Values that fall approximately below 20% their nominal value shall be considered low. Pump power shall be classified binarily as either low or nominal. Nominal pump power should be approximately 100W. Pump power that reaches or drops below 80 Watts shall be classified as low. Pump power that exceeds 80 Watts shall be considered nominal. Flow shall be classified binarily as either low or nominal. Nominal flow should be approximately 6 GPM Flow that reaches or drops below 4.7 GPM shall be considered low. Flow that exceeds 4.7 GPM shall be considered nominal.

Additionally, should the active pump signal or the flow signal be considered bad, the pump power and/or the flow signal shall be automatically classified as low.

The state of the system’s hydraulics shall be binarily determined as either nominal or failed. Additionally, the system’s hydraulics shall be dependent on the pump driving it. That is, for a primary and secondary pump, the system shall have primary and secondary hydraulics. The system’s primary hydraulics are considered to have failed if and only if any two (2) of the three (3) hydraulic parameters are considered low, whilst the primary pump is active. A primary hydraulic failure shall enable ALM-9 The system’s secondary hydraulics are considered to have failed if and only if any two (2) of the three (3) hydraulic parameters are considered low, whilst the secondary pump is active. A secondary hydraulic failure shall enable alarm ALM-10 In the event of a primary or secondary hydraulic failure, the system will attempt an automatic pump turnover. During system initialization, a system’s hydraulics status shall be overridden as nominal.

The primary and secondary hydraulic failures may be only disabled by the operator by enabling the acknowledge hydraulic fault switches (SW-10 and SW-11 respectively)

Power, pressure and flow classifications shall be fitted with hysteresis control, such that a change in classification (that is, a change from nominal to low or from low to nominal), must meet the threshold requirements listed above for at least 500ms, allowing for noise or hysteresis to be filtered out.

## Hydraulic Failure Pump Turnover

Should a hydraulic failure occur in connection with the active pump, the system shall attempt an automatic pump turnover. Should simplex mode be engaged in the event of an automatic pump turnover, the system will engage the duplex failure fault (FLT-6) and engage the shutdown sequence. Should simplex mode be disengaged, during the event of an automatic pump turnover, SW-26 shall engage, and the system shall engage a pulse sequence.

## Lifecycle Pump Monitoring & Turnover

To maximize the lifespan of the primary and secondary pump, the cooling skid shall have an automatic lifecycle pump turnover feature (i.e. pump cycling). The primary and secondary pump differential usage shall be counted using hours (i.e. ticks in the program), by a DINT-valued differential pump signal (SIG-25) Primary pump usage shall increase SIG-25 by 1 for every hour in operation. Secondary pump usage shall decrease SIG-25 by 1 for every hour in operation.  Should the pump differential signal reach 2147483646 or -2147483647 the EOTW fault (FLT-8) shall be engaged, and the system engage the shutdown sequence.

Assuming APC is disengaged: if SIG-25 reaches or surpasses 30 and the primary pump is active or SIG-25 reaches or becomes less than -30 and the secondary pump is active, the pump cycle alarm (ALM-17) shall be engaged. In all other cases, ALM-17 shall remain disengaged.

Assuming APC is engaged: if SIG-25 reaches or surpasses 30 and the primary pump is active or SIG-25 reaches or becomes less than -30 and the secondary pump is active, SIG-26 shall be engaged, and the system shall engage the pulse sequence.

## Manual Operation

The operator may choose to engage a manual pump turnover at any point during skid operation, by engaging the manual turnover switch (SW-4) Should simplex mode be engaged when attempting to engage SW4, SW4 shall disengage with no additional action. If simplex mode is disengaged when attempting to engage SW-3, SW-4 shall disengage, SW-26 shall engage and the system shall engage the pulse sequence.

# Vessel Level Control System

## Signal Processing

The vessel storing excess coolant shall be fitted with two hall sensor switches to indicate low coolant level in the vessel (P17A) and critical low coolant level in the vessel (P17B). These hall sensors shall be engaged if the coolant level within the vessel falls below the level at which the respective sensors have been installed on the vessel. The hall sensors shall be disengaged when the coolant level within the vessel is at, or surpasses, the level at which the hall sensors have been installed at.

Both hall sensors shall be integrated with hysteresis control, such that the physical signals (PHY-10 and PHY-11 respectively), shall not engage the final output signals (SIG-20, SIG-21) until at least 500 milliseconds have elapsed, in order to filter out hysteresis and noise.

## Level Monitoring

If SIG-20 is engaged, the Low Coolant Level in Vessel Alarm (ALM-2) shall be engaged. If both SIG-20 and SIG-21 are engaged, the critical vessel level fault (FLT-2) shall be engaged, and the system shall engage the shutdown sequence.

## Redundancy Control

Should SIG-21 be engaged, but SIG-20 remain disengaged, the Level Sensor Malfunction fault (FLT-4) shall engage, and the system shall engage the shutdown sequence.

# Conductivity Control System

## Signal Processing

The conductivity sensor shall communicate to the PLC using a 4-20mA WORD-valued signal (PHY-7). The WORD-valued signal shall be converted into a REAL-valued signal (SIG-7). Additionally, the conductivity sensor shall communicate integrated alarm and fault trips by communicating to the PLC through 0-24V BOOL-valued signal (PHY-8, PHY-9). The alarm and fault trip signals shall require 500ms of stability before engaging the filtered alarm and fault signals (SIG-23, SIG-24), in order to filter out hysteresis and noise.

In addition to the alarm and fault trips in the conductivity sensor, the REAL-valued signal shall also be observed for the same alarm and fault conditions. The REAL-valued signal shall be passed through a hysteresis filter, requiring 500 ms of stability before its value is classified as an alarm or fault condition.

## Conductivity Monitoring

Should the conductivity sensor alarm trip, and the REAL-valued signals observe a conductivity at or greater than 0.9 μS/cm at 25°C, the conductivity alarm (ALM-3) shall be engaged. Should the conductivity sensor alarm trip, and the conductivity sensor fault trip, and the REAL-valued signal observe a conductivity greater than 1 μS/cm at 25°C, the critical conductivity fault (FLT-3) be engaged, and the system shall engage the shutdown sequence.

## Redundancy Control

Should the conductivity sensor fault trip engage while the conductivity sensor alarm trip remains disengaged, the conductivity sensor malfunction fault (FLT-5) shall be engaged.

Should the conductivity sensor alarm trip engage, but SIG-7 fails to observe a conductivity at or greater than 0.9 μS/cm at 25°C after an elapsed time of 2 seconds, FLT-5 shall be engaged. Should SIG-7 observe a conductivity at or greater than 0.9 μS/cm at 25°C, but the conductivity alarm trip fails to engage after an elapsed time of 2 seconds, FLT-5 shall be engaged. Should both the conductivity sensor alarm trip engage, and the conductivity sensor fault trip engage, but the SIG-7 fails to register a conductivity greater than 1 μS/cm at 25°C after an elapsed time of 2 seconds, FLT-5 shall be engaged. Should the conductivity fault trip fail to engage, regardless of whether the conductivity sensor trip alarm is, or is not engaged, while SIG-7 registers a conductivity greater than 1 μS/cm at 25°C after an elapsed time of 2 seconds, FLT-5 shall be engaged.

2 seconds provides excess time such that both the analog and digital sensors of the conductivity probe may align without creating a false trip.